## Input_Variables
Column | Normal_Range_Min | Normal_Range_Max | Extended_Range_Min_Used_For_Sampling | Extended_Range_Max_Used_For_Sampling | Role_In_The_System
F36 | 0 | 40 | -10 | 50 | Input to the "General" fault system (electrical fault / low performance / undersized-oversized unit) and to the full Chiller system.
F15 | 1 | 10 | 0 | 10 | Input to the Condenser subsystem.
H25 | 28 | 35 | 18 | 45 | Input to the Condenser and General subsystems, and to the full Chiller system.
H24 | 40 | 55 | 30 | 65 | Input to the Compressor subsystem and to the full Chiller system.
H64 | 28 | 38 | 16 | 50 | Shared input across Chiller, Condenser, Compressor and General (a highly influential cross-cutting variable).
H15 | 50 | 75 | 35 | 90 | Input to the Compressor subsystem and to the full Chiller system.
F14 | 1 | 160 | 0 | 160 | Input to the General subsystem and to the full Chiller system.
H42 | 4.5 | 11 | 1.6875 | 13.8125 | Input to the Compressor subsystem and to the full Chiller system.
Mode_1Cool_2Heat | - | - | - | - | Mode selector: Cool=1 / Heat=2. Determines whether H23F (Cool) or H23C (Heat) is used as the real reading; the other variable is replaced by the midpoint of its extended range.
H23F | 3 | 10 | 0 | 13 | Input to the Compressor subsystem and to the full Chiller system, only active in Cool mode (Mode=1).
H23C | 8 | 12 | 6 | 14 | Input to the Compressor subsystem and to the full Chiller system, only active in Heat mode (Mode=2).
P02 | 0.1 | 0.8 | 0 | 1.5 | Input to the Evaporator subsystem and to the full Chiller system.
H20 | 0.1 | 5 | 0 | 5 | Input to the Evaporator subsystem and to the full Chiller system.
P03 | 1.5 | 3 | 0 | 4.5 | Input to the Evaporator subsystem and to the full Chiller system. Note: in the original MATLAB script, if this value exceeds the extended upper bound it is forced to 4.5 instead of being clipped to the max (a possible quirk/bug in the source code, faithfully replicated here).
F37 | 8 | 20 | 3 | 24 | Used together with F39 to derive T05 = F37 - F39 (evaporator temperature difference). Also a direct input to the General subsystem.
F39 | 3 | 15 | -1 | 22 | Used together with F37 to derive T05. Also a direct input to the General subsystem.
H62 | 0 | 1 | 0 | 1 | Binary variable (0/1) used in the Evaporator subsystem and the full Chiller system.
T05 (derived) | 0 | 5 | 0 | 8 | Not sampled directly: computed as F37 - F39 and clipped to the extended range. Input to the Evaporator subsystem and the full Chiller system.

## Output_Variables_Targets
Column | System_Level | Meaning
Chiller_Condenser_Fault | Chiller (machine level) | Probability of a condenser-related fault
Chiller_ExpansionValve_Fault | Chiller | Probability of an expansion valve fault (no dedicated subsystem exists for it)
Chiller_Evaporator_Fault | Chiller | Probability of an evaporator-related fault
Chiller_Compressor_Fault | Chiller | Probability of a compressor-related fault
Chiller_General_Fault | Chiller | Probability of a general chiller fault
Condenser_Valve_Fault | Condenser (subsystem) | Probability of a fault in the condenser valve
Condenser_Filter_Fault | Condenser | Probability of a fault in the condenser filter
Condenser_GasChargeNeeded | Condenser | Probability that the unit needs a refrigerant gas recharge
Condenser_Fan_Fault | Condenser | Probability of a fan fault
Condenser_Coil_Fault | Condenser | Probability of a coil/battery fault
Condenser_GasLeak | Condenser | Probability of a refrigerant gas leak
Evaporator_LiquidLeak | Evaporator (subsystem) | Probability of a liquid leak
Evaporator_Valve_Fault | Evaporator | Probability of a fault in the evaporator valve
Evaporator_StrainerFilter_Fault | Evaporator | Probability of a fault in the strainer filter
Evaporator_Piping_Fault | Evaporator | Probability of a fault in the piping
Evaporator_HeatExchanger_Fault | Evaporator | Probability of a fault in the heat exchanger
Evaporator_Electrical_Fault | Evaporator | Probability of an electrical fault in the evaporator
Evaporator_FlowSwitch_Fault | Evaporator | Probability of a fault in the flow switch
Compressor_General_Fault | Compressor (subsystem) | Probability of a general compressor fault
Compressor_Contactor_Fault | Compressor | Probability of a fault in the contactor
Compressor_Leak | Compressor | Probability of a leak in the compressor
Compressor_OilLoss | Compressor | Probability of oil loss
Compressor_SuperheatIncreaseNeeded | Compressor | Probability that superheat needs to be increased
General_Electrical_Fault | General (subsystem) | Probability of a general electrical fault
General_LowPerformance | General | Probability of low performance
General_UnitUndersizedOversized | General | Probability that the chiller unit is mis-sized for the installation

## Meta_Columns
Column | Meaning
Sample_ID | Unique row identifier.
Split | "train" = one of the 12,000 freshly generated, non-duplicated samples. "holdout_manual" = one of the 30 original hand-crafted test scenarios (BateriaPruebas.xlsx) - use this only for a final sanity check, never for training.
Rule_ID | Only filled for holdout_manual rows: the original rule name (Rule 1, Rule 2, ...).
Expected_Fault_Label | Only filled for holdout_manual rows: the single fault category the original author expected this scenario to trigger (None / Condenser / Expansion_Valve / Evaporator / Compressor / General). Empty for train rows since those use continuous multi-output probability labels instead.